We have kg/hr of steam, now calculate volumetric flow requirement:

Get specific volume of steam for corresponding temperature and pressure:

SV = specific volume m3/kg

Volumetric Flow Rate =VFR=m3/hr

VFR = SV x Steam Qty (kg/hr)

Velocity Selection (Assume initially) = 30m/s (can be between only 20-40m/s)

VFR = Area x Velocity

Therefore, Dia = Square Root ((4 x VFR)/(π x Velocity))

Now let’s check the pressure drop: