## Steam DB
Pressure (barg) | Sat Temp (°C) | hf (kJ/kg) | hfg (kJ/kg) | hg (kJ/kg) | Specific Volume Steam (m3/kg)
0 | 100 | 419 | 2257 | 2676 | 1.694
1 | 120.2 | 505 | 2202 | 2707 | 0.885
2 | 133.5 | 561 | 2164 | 2725 | 0.605
3 | 143.6 | 605 | 2133 | 2738 | 0.462
4 | 151.8 | 640 | 2108 | 2748 | 0.375
5 | 158.8 | 671 | 2085 | 2756 | 0.315
6 | 164.9 | 698 | 2065 | 2763 | 0.271
7 | 170.4 | 722 | 2047 | 2769 | 0.238
8 | 175.4 | 744 | 2030 | 2774 | 0.212
9 | 179.9 | 764 | 2015 | 2779 | 0.191
10 | 184.1 | 782 | 2001 | 2783 | 0.174
12 | 191.6 | 815 | 1974 | 2789 | 0.148
15 | 198.3 | 844 | 1950 | 2794 | 0.132
20 | 212.4 | 908 | 1889 | 2797 | 0.099
25 | 224 | 962 | 1835 | 2797 | 0.081
30 | 233.9 | 1008 | 1788 | 2796 | 0.068
40 | 250.4 | 1087 | 1708 | 2795 | 0.05
50 | 264 | 1155 | 1638 | 2793 | 0.039
60 | 275.6 | 1215 | 1576 | 2791 | 0.032
80 | 295.1 | 1318 | 1468 | 2786 | 0.022
100 | 311.1 | 1405 | 1374 | 2779 | 0.016
hf = Enthalpy of Saturated Liquid
Saturation Temperature (Tsat) This is the temperature at which: Water starts boiling. Steam starts condensing.
hfg = Latent Heat of Vaporization
hg = Enthalpy of Saturated Steam
Specific Volume of Steam

## Pipe DB
Nominal Pipe Size (NPS) | Diameter Nominal (DN) | OD (mm) | SCH 40 Thickness (mm) | Schedule | Weight (kg/m)
1/8 | 6 | 10.3 | 1.73 | 40 | 0.37
1/4 | 8 | 13.7 | 2.24 | 40 | 0.84
3/8 | 10 | 17.1 | 2.31 | 40 | 1.27
1/2 | 15 | 21.3 | 2.77 | 40 | 1.69
3/4 | 20 | 26.7 | 2.87 | 40 | 2.5
1 | 25 | 33.4 | 3.38 | 40 | 3.39
1-1/4 | 32 | 42.2 | 3.56 | 40 | 4.05
1-1/2 | 40 | 48.3 | 3.68 | 40 | 5.44
2 | 50 | 60.3 | 3.91 | 40 | 8.63
2-1/2 | 65 | 73 | 5.16 | 40 | 11.29
3 | 80 | 88.9 | 5.49 | 40 | 13.57
4 | 100 | 114.3 | 6.02 | 40 | 16.07
5 | 125 | 141.3 | 6.55 | 40 | 21.77
6 | 150 | 168.3 | 7.11 | 40 | 28.26
8 | 200 | 219.1 | 8.18 | 40 | 42.55
10 | 250 | 273 | 9.27 | 40 | 60.31
12 | 300 | 323.9 | 10.31 | 40 | 79.73
14 | 350 | 355.6 | 11.13 | 40 | 94.55
16 | 400 | 406.4 | 12.7 | 40 | 123.3
18 | 450 | 457 | 14.27 | 40 | 155.8
20 | 500 | 508 | 15.09 | 40 | 183.42
24 | 600 | 609.6 | 17.48 | 40 | 255.41
1/8 | 6 | 10.3 | 2.41 | 80 | 0.47
1/4 | 8 | 13.7 | 3.02 | 80 | 0.8
3/8 | 10 | 17.1 | 3.2 | 80 | 1.1
1/2 | 15 | 21.3 | 3.73 | 80 | 1.62
3/4 | 20 | 26.7 | 3.91 | 80 | 2.2
1 | 25 | 33.4 | 4.55 | 80 | 3.24
1-1/4 | 32 | 42.2 | 4.85 | 80 | 4.47
1-1/2 | 40 | 48.3 | 5.08 | 80 | 5.41
2 | 50 | 60.3 | 5.54 | 80 | 7.48
2-1/2 | 65 | 73 | 7.01 | 80 | 11.41
3 | 80 | 88.9 | 7.62 | 80 | 15.27
4 | 100 | 114.3 | 8.56 | 80 | 22.32
5 | 125 | 141.3 | 9.53 | 80 | 30.97
6 | 150 | 168.3 | 10.97 | 80 | 42.56
8 | 200 | 219.1 | 12.7 | 80 | 64.64
10 | 250 | 273 | 15.09 | 80 | 95.98
12 | 300 | 323.9 | 17.48 | 80 | 132.05
14 | 350 | 355.6 | 19.05 | 80 | 158.11
16 | 400 | 406.4 | 21.44 | 80 | 203.54
18 | 450 | 457 | 23.83 | 80 | 254.57
20 | 500 | 508 | 26.19 | 80 | 311.19
24 | 600 | 609.6 | 30.96 | 80 | 442.11

## Velocity Limits
Condition | Velocity
m/s
Initial | 30
Maximum | 40
Minimum | 20

## Friction Factors
Nominal Size | Friction Factor
15 | 0.027 | New carbon steel pipe: f = 0.020
20 | 0.025 | Existing/aged carbon steel pipe: f = 0.025
25 | 0.023 | Conservative estimate: f = 0.030
32 | 0.022
40 | 0.021
50 | 0.019
65 | 0.018
80 | 0.018
100 | 0.017
125 | 0.016
150 | 0.015
200 | 0.014
250 | 0.014
300 | 0.013
400 | 0.013
450 | 0.012
600 | 0.012

## Fittings DB
Component | Le/D
90° LR Elbow | 30
90° SR Elbow
45° Elbow | 16
Tee Run | 20
Tee Branch | 60
Concentric Reducer | 10
Gate Valve | 8
Globe Valve | 340
Ball Valve
Swing Check Valve | 100
Y-Strainer | 60
Separator

## Steam Trap Data
Condensate Pressure Before Trap | Flash Steam to Atmosphere
2 barg | 7%
4 barg | 12%
6 barg | 15%
8 barg | 18%
10 barg | 20%

## Pipe Support
Pipe Size | Support Spacing
15-25 NB | 2.5 m
32-50 NB | 3.0 m
65-100 NB | 4.0 m
125-150 NB | 5.0 m