- Determine pipe ID – calculated in previous module (D)

- Calculate steam velocity – take from datasheet for V1

- Calculate total equivalent length:

For fittings: Le​=(Le/D​​)×D, Where Le/D is to be picked up from equivalent length sheet

- Calculate effective length. (Sum of Pipe length and equivalent fitting lengths)

- Apply Darcy-Weisbach using effective length.

- Report pressure drop.

Pressure drop = Friction factor x (L/D) x (density x Velocity2 / 2)

Density = 1/(Specific Volume)

Friction Factor = 0.025 (For V1)

Based on the Diameter calculated in steam pipe sizing module, select a closest (larger or Smaller one) standard pipe.

Refer to Pipe dimensions table and get the new ID. Using the new ID recalculate the velocity.

Using the new ID size and velocity calculated, now calculate the Pressure drop and check if it is acceptable.

How to check if Pressure drop is acceptable:

(Calculated pressure drop) < (Starting pressure – required steam pressure at equipment)

If not acceptable select the next larger size Standard pipe and repeat.