Inputs

- Condensate load (kg/hr)

- Pressure before trap

- Pressure after trap

- Pipe length

- Fittings

Intermediate Calculations

- Flash steam %

- Liquid flow

- Flash steam flow

- Two-phase volumetric flow

Outputs

- Recommended pipe size

- Velocity

- Pressure drop

- Estimated backpressure

Flash Steam %=(​hf1​−hf2)​​×100 / hfg2

where:

- hf1​ = condensate enthalpy before trap

- hf2​ = saturated liquid enthalpy at downstream pressure

- hfg2​ = latent heat at downstream pressure

VFR for Flash steam= SV x Flash steam Qty (kg/hr)

VFR for condensate after trap = [total condensate formed (kg/hr) – Flash steam Qty (kg/hr)] x SV of condensate (approx. 1)

Total VFR after trap = VFR for Flash steam + VFR for condensate after trap

Velocity Selection (Assume initially) = 30m/s (can be between only 20-40m/s)

VFR = Area x Velocity

Therefore, Dia = Square Root ((4 x VFR)/(π x Velocity))